# BS 5266-1:2016
Emergency Lighting Systems compliance checklist

Deviations highlighted in bold type are considered to be potential system integrity or life threats and are not considered to be acceptable deviations against the recommendations of BS 5266-1:2016.

If deviations of this nature are identified during a site inspection, this could result in a major non-compliance being issued.

| Certificated / applicant company: |  |  |  |
| --- | --- | --- | --- |
| Company representatives: |  |  |  |
| Customer / user: |  |  |  |
| Location: |  |  |  |
| User representatives: |  |  |  |
| Restrictions made by user: (e.g. access and performance of tests) |  |  |  |
| Auditor: |  |  |  |
| Date of audit: |  |  |  |
| Applicable modules | System design |  |  |
|  | Installation |  |  |
|  | Commissioning and handover (inc. verification) |  |  |

Note: This checklist does not cover maintenance

| Name of company undertaking system design: |  |  |  |
| --- | --- | --- | --- |
| A01 Module certificate issued: | Yes | No | N/A |
| Certificate number: |  |  |  |
| Date: |  |  |  |

| Name of company undertaking installation: |  |  |  |
| --- | --- | --- | --- |
| A01 Module certificate issued: | Yes | No | N/A |
| Certificate number: |  |  |  |
| Date: |  |  |  |

| Name of company undertaking commissioning & handover: |  |  |  |
| --- | --- | --- | --- |
| A01 Module certificate issued: | Yes | No | N/A |
| Certificate number: |  |  |  |
| Date: |  |  |  |

| A01 NSI Certificate of Select as appropriate issued: | Yes | No |
| --- | --- | --- |
| Certificate number: |  |  |
| Date: |  |  |
| Record agreed deviations below (or attach copy of certificate with list of deviations): |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| DESIGN MODULE |  |  |  |  |
|  | Specified standards applied: |  | BS 5266-1 |  |
|  | Specify whether system is Addressable (A) or Non-Addressable (N) |  | A N |  |
| A02 | BS 5266 Type/Classification of system specified: X1****180 etc. : |  |  | BS 5266-1 Annex F |
| A03 | Is there evidence that consultation has taken place with all interested parties? |  | Yes No | BS 5266-1 4.1 |
| A04 | Is the type and classification of system appropriate and as specified in contract? |  | Yes No | BS 5266-1 6.7 & Annex F |
| A05 | Is the specified ELS duration period suitable for the category of system and the level of supervision? |  | Yes No | BS 5266-1 Section 9 |
| A06 | Has the designer obtained the required information before commencing the system design? |  | Yes No | BS 5266-1 10.2 |
| A07 | Have suitable plans of the building been provided to the designer prior to the design process commencing? |  | Yes No | BS 5266-1 4.2 |
| A08 | Have illuminance calculations been carried out or has the designer referred to the manufacturers’ photometric data/spacing tables? |  | N/A Yes No | BS 5266-1 10.3 |
| A09 | Has all the relevant information been obtained to enable the design of the electrical installation supplying the ELS? |  | N/A Yes No | BS 5266-1 10.4/10.5 |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| DOCUMENTATION |  |  |  |  |
| B01 | Are there satisfactory commissioning records? |  | N/A Yes No | BS 5266-1 BS 5266-8 |
| B02 | Have BS 5266 certificates for design, installation, verification & completion been issued? (as applicable) |  | Yes No | BS 5266-1 11 Annex (H1 to H4) |
| B03 | Is there a record of agreed deviations? |  | N/A Yes No | BS 5266-1 Annex H1 |
| B04 | Have suitable user instructions/manuals been provided to the customer? |  | N/A Yes No | BS 5266-1 10.6/10.7 |
| B05 | Are there satisfactory 'as fitted' drawings? |  | N/A Yes No | BS 5266-8 6.1 |
| B06 | Have the drawings been signed by a nominated designer? |  | N/A Yes No | BS 5266-8 6.1 |
| B07 | Have 'as fitted' drawings been provided to the customer? |  | N/A Yes No | BS 5266-8 6.1 |
| B08 | Has a logbook been provided to the customer which meets the guidance given in Annex J of BS 5266-1:2016? |  | N/A Yes No | BS 5266-1 11 BS5266-8 6.1/6.3 |
| B09 | Are the relevant BS 7671 test records available & Satisfactory? |  | N/A Yes No | BS 5266-1 8.1 |
| B10 | Is BS7671 and photometric data referenced on the installation/verification certification? |  | Yes No | BS5266-1 Annex H |
| B11 | Where Lux readings were taken to verify conformity, are there minimum and maximum level recorded? |  | N/A Yes No | BS EN1038 4.2.2/4.3.2 |
| B12 | Where Lux readings were taken to verify conformity, were appropriate derating factors applied to the readings taken and recommendations of Annex D considered? |  | N/A Yes No | BS 5266-1 Annex D |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| CENTRAL POWER SUPPLY SYSTEMS |  |  |  |  |
| C01 | Are cables of a suitable type? |  | Yes No | BS 5266-1 8.2.2 (a)(b)(c)(d) |
| C02 | Are cables adequately protected against mechanical damage? |  | N/A Yes No | BS 5266-1 8.2.5/8.2.11 |
| C03 | Are methods of cable support satisfactory? |  | N/A Yes No | BS 5266-1 8.2.3 |
| C04 | Is there suitable segregation from other services and other fire alarm cables, where required? |  | N/A Yes No | BS 5266-1 8.2.6 |
| C05 | Are joints in cables terminated correctly? ie. Fire resisting Material? (applies only to joints external to ELS system components) |  | N/A Yes No | BS 5266-1 8.2.4 |
| C06 | Are all junction boxes suitably labelled? |  | N/A Yes No | BS 5266-1 8.2.4 |
| C07 | Does each conductor have a CSA of at least 1.5mm2? |  | N/A Yes No | BS 5266-1 8.2.7 |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| MAINS POWER SUPPLIES (GENERAL) |  |  |  |  |
| D01 | Has a suitable mains supply been provided? |  | N/A Yes No | BS 5266-1 8.3.1 |
|  | Specifically: |  |  |  |
| D02 | Is the continuity of supply satisfactory including ‘Rest Mode ‘where applicable? |  | Yes No | BS 5266-1 8.3.2 |
| D03 | Are isolators, switches and other protective devices protected from unauthorised operation? |  | Yes No | BS 5266-1 8.3.2 |
| D04 | Is labelling satisfactory? |  | Yes No | BS 5266-1 8.3.2/8.3.4 |
| D05 | Have suitable test facilities been provided for the ELS (avoiding isolation of a required service)? |  | Yes No | BS 5266-1 8.3.3 |
| D06 | Is wiring of a suitable type? |  | Yes No | BS 5266-1 8.1 |
| D07 | Where an automatic test facility is in place, is the system configured to test alternative luminaires? |  | N/A Yes No | BS 5266-1 8.3.3 |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| LUMINAIRES |  |  |  |  |
| E01 | Do luminaires meet the requirements of BS EN 60598-2-22? |  | N/A Yes No | BS 5266-8 5.5.1 |
| E02 | Is luminaire siting appropriate for the area being illuminated and/or sufficient for the building in which they are installed? |  | Yes No | BS 5266 |
| E03 | Are luminaires mounted at least 2m above floor level? |  | Yes No | BS EN 1038 4.1.1 |
| E04 | Are luminaires mounted below smoke reservoirs? |  | N/A Yes No | BS 5266-1 6.4 |
|  | Specifically, is siting/spacing satisfactory in relation to: |  |  |  |
| E05 | Emergency exit doors? |  | N/A Yes No | BS 5266-1 5.2.8.1(a) |
| E06 | Flights of stairs & any other change in level? |  | N/A Yes No | BS 5266-1 5.2.8.1 (b)(c) |
| E07 | Mandatory emergency exit & safety signs? |  | N/A Yes No | BS 5266-1 5.2.8.1 (d) |
| E08 | Each change in direction? |  | N/A Yes No | BS 5266-1 5.2.8.1 (e) |
| E09 | Intersections of corridors? |  | N/A Yes No | BS 5266-1 5.2.8.1 (f) |
| E10 | Near each first aid post? |  | N/A Yes No | BS 5266-1 5.2.8.1 (h) |
| E11 | Outside and near to each final exit door and routes to a place of safety? |  | N/A Yes No | BS 5266-1 5.2.8.1 (g) & 5.2.8.2 |
| E12 | Near each piece of firefighting equipment and manual call point? |  | N/A Yes No | BS 5266-1 5.2.8.1 (i) |
| E13 | Near any escape equipment provided for disabled people |  | N/A Yes No | BS 5266-1 5.2.8.1 (j) |
| E14 | Near refuges and call points inc. two-way communication systems. |  | N/A Yes No | BS 5266-1 5.2.8.1 (k) |
| E15 | Near disabled toilet alarm call position |  | N/A Yes No | BS 5266-1 5.2.8.1 (k) |
| E16 | Manual release controls which release electronically locked doors |  | N/A Yes No | BS 5266-1 5.2.8.1 (l) |
| E17 | Evacuation lift cars? |  | N/A Yes No | BS 5266-1/5.2.8.3 |
| E18 | Moving stairways & walkways? |  | N/A Yes No | BS 5266-1/5.2.8.4 |
| E19 | Toilet facilities? |  | N/A Yes No | BS 5266-1/5.2.8.5 |
| E20 | Motor generator, control & plant rooms? |  | N/A Yes No | BS 5266-1/5.2.8.6 |
| E21 | Covered car parks? |  | N/A Yes No | BS 5266-1/5.2.8.7 |
| E22 | Is an “exit” or “directional” sign in view along all points of the escape route(s) |  | N/A Yes No | BS 5266-8/4.2 |
| E23 | Escape route(s)? |  | N/A Yes No | BS 5266-8/4.3 |
| E24 | Open areas >60m2 or smaller areas if used by a large number of people? |  | N/A Yes No | BS 5266-8/4.4 |
| E25 | High risk task areas? |  | N/A Yes No | BS 5266-8/4.5 |
| E26 | Are the luminaires orientated in accordance with the design to ensure correct spacing? |  | Yes No | BS 5266-1 Clause 6 |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| EMERGENCY LIGHTING SYSTEM INTEGRITY |  |  |  |  |
| F01 | Do luminaires operate in the event of a local lighting circuit failure? |  | Yes No | BS 5266-8 5.2 |
| F02 | Has each compartment of the ELS been fitted with at least two luminaires? |  | Yes No | BS 5266-8 5.3 |
| F03 | Has each open area been fitted with at least two luminaires? |  | N/A Yes No | BS 5266-8 5.3 |
| F04 | Are first aid posts and firefighting equipment/MCPs NOT ON escape routes illuminated to at least 5 lx at floor level? |  | N/A Yes No | BS EN 1038 4.1.2(i) |
| F05 | Are escape routes up to 2m wide illuminated to at least 1 lx on the centre line and to at least 50% of the above value across the central band (at least 50% of the route width)? |  | Yes No | BS EN 1038 4.2.1 |
| F06 | Is the minimum duration of the emergency escape lighting at least 1 hour? |  | Yes No | BS EN 1038 4.2.5 |
| F07 | Is the ratio of illuminance (max to min) along the centre line of escape route(s) and open area lighting not greater than 40:1? |  | Yes No | BS EN 1038 4.2.2/4.3.2 |
| F08 | Does escape route lighting, open area lighting and safety signs achieve 50% of the required level within 5 secs and 100% within 60 secs? |  | Yes No | BS EN 1038 4.2.6/4.3.6/5.1 |
| F09 | For open area (anti-panic) lighting is the illuminance level at least 0.5 lx at floor level (excluding 0.5m around the perimeter of the area)? |  | N/A Yes No | BS EN 1038 4.3.1 |
| F10 | Is the minimum duration of the open area lighting at least 1 hour? |  | N/A Yes No | BS EN 1038 4.3.5 |
| F11 | In high risk areas, is the illuminance level at least 10% of the required level for that task, and, not less than 15 lx? |  | N/A Yes No | BS EN 1038 4.4.1 |
| F12 | Is the minimum duration of high risk lighting equal to at least the period for which the risk exists to people? |  | N/A Yes No | BS EN 1038 4.4.5 |
| F13 | Have high risk areas been provided with maintained luminaires or is the full required illuminance achieved within 0.5 secs? |  | N/A Yes No | BS EN 1038 4.4.6 |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| ILLUMINANCE OF SPECIFIC LOCATIONS |  |  |  |  |
| Is the minimum light level and duration achieved for the following specific locations: |  |  |  |  |
| G01 | KITCHENS 15 Lux for 30 Minutes |  | N/A Yes No | BS5266-1 Table E1 |
| G02 | FIRST AID ROOMS 15 Lux for 30 Minutes |  | N/A Yes No | BS5266-1 Table E1 |
| G03 | EXAMINATION & TREATMENT ROOMS 50 Lux for 30 Minutes |  | N/A Yes No | BS5266-1 Table E1 |
| G04 | REFUGE AREAS FOR PEOPLE WITH MOBILITY IMPAIRMENTS. 5 Lux for Full Rated Duration |  | N/A Yes No | BS5266-1 Table E1 |
| G05 | PLANT/SWITCH/WINDING ROOMS 15 Lux for Full Rated Duration |  | N/A Yes No | BS5266-1 Table E1 |
| G06 | FIRE ALARM CIE 15 Lux for Full Rated Duration |  | N/A Yes No | BS5266-1 Table E1 |
| G07 | RECEPTION AREAS 15 Lux for Full Rated Duration |  | N/A Yes No | BS5266-1 Table E1 |
| G08 | PANIC BARS/PADS/SECURITY DEVICES AT EXIT DOORS 5 Lux for Full Rated Duration |  | N/A Yes No | BS5266-1 Table E1 |
| G09 | SURROUNDS OF SWIMMING POOLS, SWIMMING AREAS, DIVING PLATFORMS & FLUMES. 5 Lux for Full Rated Duration |  | N/A Yes No | BS5266-1 Table E1 |
| Comments: |  |  |  |  |

|  |  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- | --- |
| WORKMANSHIP |  |  |  |  |  |
| H01 | What is the standard of workmanship? |  | Good Satisfactory |  |  |
|  |  |  | Unsatisfactory Poor |  |  |
| H02 | Does the system conform to BS 7671 (as far as can be ascertained)? |  | Yes No |  | 8 |
| H03 | Are cables securely fixed? |  | N/A Yes No |  | 8.2.3 |
| Comments: |  |  |  |  |  |