# BS 5266-1:2016

# Emergency Lighting Systems (Maintenance)
compliance checklist

Deviations highlighted in bold type are considered to be potential system integrity or life threats and are not considered to be acceptable deviations against the recommendations of BS 5266-1:2016.

If deviations of this nature are identified during a site inspection, this could result in a major non-compliance being issued.

| Certificated / applicant company: |  |
| --- | --- |
| Company representatives: |  |
| Customer / user: |  |
| Location: |  |
| User representatives: |  |
| Restrictions made by user: (e.g. access and performance of tests) |  |
| Auditor: |  |
| Date of audit: |  |

| Name of company that installed system (if known) |  |
| --- | --- |
| Completion date of ELS (if known) |  |
| Date system taken over for maintenance |  |

Record agreed deviations below (Identified by company on verification or maintenance visits):

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| GENERAL / DOCUMENTATION |  |  |  |  |
|  | Specified standards applied: |  | BS 5266-1 |  |
|  | BS 5266 Type / Classification of system specified: |  |  | BS 5266-1 Annex F |
| A01 | Are original design records and site plans available OR have company created site plans? |  | Yes No | BS 5266-1 4.2, Annex L.4 |
| A02 | Is the category of system appropriate and ELS duration period suitable for the category of system and the level of supervision? |  | Yes No | BS 5266-1 6.7 |
| A03 | Is authenticated spacing data available for existing installations or are estimates available and acceptable? |  | N/A Yes No | BS 5266-1 Annex G |
| A04 | Where no illuminance calculations are available, have the company measured lux levels to ensure that these are sufficient. |  | N/A Yes No | BS 5266-1 Annex D |
| A05 | If original records are not available, have the company carried out verification of the existing system in accordance with Annex K? |  | N/A Yes No | BS 5266-1 11 Annex K |
| A06 | Where original records are not available has maintaining company issued a verification checklist in accordance with Annex K? |  | N/A Yes No | BS 5266-1 11 Annex K |
| A07 | Are there records of agreed deviations either from original records or identified by maintenance company? |  | N/A Yes No | BS 5266-1 Annex K |
| A08 | Have suitable user instructions/manuals been provided to the customer? |  | N/A Yes No | BS 5266-1 10.6 |
| A09 | Is there a logbook available? If not, have the maintaining company offered to provide one? |  | N/A Yes No | BS 5266-1 11+ Annex J BS 5266-8 6.3 |
| A10 | Does the logbook detail the required information i.e. date of commissioning (if known), date of periodic test, date of maintenance, dates of remedial action, dates of any alterations, mode of operation of automatic testing (if applicable). |  | N/A Yes No | BS 5266-8 6.3 BS 5266-1 11+ Annex J |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| SERVICING AND TESTING |  |  |  |  |
| B01 | Has the user been made aware of the limitations of the system during and after testing? |  | Yes No | BS 5266-8 7.2.1 |
| B02 | Is there evidence that users are checking visual indicators of central battery units on a daily basis? |  | N/A Yes No | BS 5266-8 7.2.2 |
| B03 | Is there evidence that users are carrying out monthly testing? |  | Yes No | BS 5266-8 7.2.3 |
| B04 | Have the luminaires been tested for their full rated duration and LED’s checked annually? |  | Yes No | BS 5266-8 7.2.4(a) |
| B05 | On completion of full duration testing are charging indicators/devices checked to ensure that the mains supply has been restored? |  | Yes No | BS 5266-8 7.2.4(b) |
| B06 | Where automatic testing devices are used, are the results of monthly and annual testing recorded? |  | N/A Yes No | BS 5266-8 7.2.3 / 7.2.4 |
| B07 | Has a periodic inspection and test certificate been issued in accordance with Annex M? |  | Yes No | BS 5266-1 11 |
| B08 | Have the dates and results of annual testing been recorded in the system logbook? |  | N/A Yes No | BS 5266-8 7.2.4(c) |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| CENTRAL POWER SUPPLY SYSTEMS |  |  |  |  |
| C01 | Are cables of a suitable type? |  | Yes No | BS 5266-1 8.2.2 (a)(b)(c)(d) |
| C02 | Are cables adequately protected against mechanical damage? |  | N/A Yes No | BS 5266-1 8.2.5/8.2.11 |
| C03 | Are methods of cable support satisfactory? |  | N/A Yes No | BS 5266-1 8.2.3 |
| C04 | Is there suitable segregation from other services and other fire alarm cables, where required? |  | N/A Yes No | BS 5266-1 8.2.6 |
| C05 | Are joints in cables terminated correctly with Fire Resistant connections? (applies only to joints external to ELS system components) |  | N/A Yes No | BS 5266-1 8.2.4 |
| C06 | Are all junction boxes suitably labelled? |  | N/A Yes No | BS 5266-1 8.2.4 |
| C07 | Does each conductor have a CSA of at least 1.5mm2? |  | N/A Yes No | BS 5266-1 8.2.7 |
| C08 | Have battery terminals been checked and checks carried out for battery leaks? |  | N/A Yes No | BS 5266-1 13.3.2 |
| C09 | Has electrolyte level been checked as per manufacturer’s recommendations (where applicable)? |  | N/A Yes No | BS 5266-1 13.3.2 |
| C10 | Have replacement batteries been checked for compatibility? |  | N/A Yes No | BS 5266-1 13.3.2 |
| C11 | Have generators been checked as per manufacturer’s recommendations? |  | N/A Yes No | BS 5266-1 13.3.2 |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| MAINS POWER SUPPLIES (GENERAL) |  |  |  |  |
| D01 | Has a suitable mains supply been provided? |  | N/A Yes No | BS 5266-1 8.3.1 |
|  | Specifically: |  |  |  |
| D02 | Is the continuity of supply satisfactory including ‘Rest Mode ‘where applicable? |  | Yes No | BS 5266-1 8.3.2 |
| D03 | Are isolators, switches and other protective devices protected from unauthorised operation? |  | Yes No | BS 5266-1 8.3.2 |
| D04 | Is labelling satisfactory? |  | Yes No | BS 5266-1 8.3.2/8.3.4 |
| D05 | Have suitable test facilities been provided for the ELS (avoiding isolation of a required service)? |  | Yes No | BS 5266-1 8.3.3 |
| D06 | Is wiring of a suitable type? |  | Yes No | BS 5266-1 8.1 |
| D07 | Where an automatic test facility is in place, is the system configured to test alternative luminaires? |  | N/A Yes No | BS 5266-1 8.3.3 |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| LUMINAIRES |  |  |  |  |
| E01 | Do luminaires meet the requirements of BS EN 60598-2-22? |  | N/A Yes No | BS 5266-8 5.5.1 |
| E02 | Is luminaire siting appropriate for the area being illuminated and/or sufficient for the building in which they are installed? |  | Yes No | BS 5266 |
| E03 | Are luminaires mounted at least 2m above floor level? |  | Yes No | BS EN 1038 4.1.1 |
| E04 | Are luminaires mounted below smoke reservoirs? |  | N/A Yes No | BS 5266-1 6.4 |
|  | Specifically, is siting/spacing satisfactory in relation to: |  |  |  |
| E05 | Emergency exit doors? |  | N/A Yes No | BS 5266-1 5.2.8.1(a) |
| E06 | Flights of stairs & any other change in level? |  | N/A Yes No | BS 5266-1 5.2.8.1 (b)(c) |
| E07 | Mandatory emergency exit & safety signs? |  | N/A Yes No | BS 5266-1 5.2.8.1 (d) |
| E08 | Each change in direction? |  | N/A Yes No | BS 5266-1 5.2.8.1 (e) |
| E09 | Intersections of corridors? |  | N/A Yes No | BS 5266-1 5.2.8.1 (f) |
| E10 | Near each first aid post? |  | N/A Yes No | BS 5266-1 5.2.8.1 (h) |
| E11 | Outside and near to each final exit door and routes to a place of safety? |  | N/A Yes No | BS 5266-1 5.2.8.1 (g) & 5.2.8.2 |
| E12 | Near each piece of firefighting equipment and manual call point? |  | N/A Yes No | BS 5266-1 5.2.8.1 (i) |
| E13 | Near any escape equipment provided for disabled people |  | N/A Yes No | BS 5266-1 5.2.8.1 (j) |
| E14 | Near refuges and call points inc. two-way communication systems. |  | N/A Yes No | BS 5266-1 5.2.8.1 (k) |
| E15 | Near disabled toilet alarm call position |  | N/A Yes No | BS 5266-1 5.2.8.1 (k) |
| E16 | Manual release controls which release electronically locked doors |  | N/A Yes No | BS 5266-1 5.2.8.1 (l) |
| E17 | Evacuation lift cars? |  | N/A Yes No | BS 5266-1/5.2.8.3 |
| E18 | Moving stairways & walkways? |  | N/A Yes No | BS 5266-1/5.2.8.4 |
| E19 | Toilet facilities? |  | N/A Yes No | BS 5266-1/5.2.8.5 |
| E20 | Motor generator, control & plant rooms? |  | N/A Yes No | BS 5266-1/5.2.8.6 |
| E21 | Covered car parks? |  | N/A Yes No | BS 5266-1/5.2.8.7 |
| E22 | Is an “exit” or “directional” sign in view along all points of the escape route(s) |  | N/A Yes No | BS 5266-8/4.2 |
| E23 | Escape route(s)? |  | N/A Yes No | BS 5266-8/4.3 |
| E24 | Open areas >60m2 or smaller areas if used by a large number of people? |  | N/A Yes No | BS 5266-8/4.4 |
| E25 | High risk task areas? |  | N/A Yes No | BS 5266-8/4.5 |
| E26 | Are the luminaires orientated in accordance with the design to ensure correct spacing? |  | Yes No | BS 5266-1 Clause 6 |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| EMERGENCY LIGHTING SYSTEM INTEGRITY |  |  |  |  |
| F01 | Do luminaires operate in the event of a local lighting circuit failure? |  | Yes No | BS 5266-8 5.2 |
| F02 | Has each compartment of the ELS been fitted with at least two luminaires? |  | Yes No | BS 5266-8 5.3 |
| F03 | Has each open area been fitted with at least two luminaires? |  | N/A Yes No | BS 5266-8 5.3 |
| F04 | Are first aid posts and firefighting equipment/MCPs NOT ON escape routes illuminated to at least 5 lx at floor level? |  | N/A Yes No | BS EN 1038 4.1.2(i) |
| F05 | Are escape routes up to 2m wide illuminated to at least 1 lx on the centre line and to at least 50% of the above value across the central band (at least 50% of the route width)? |  | Yes No | BS EN 1038 4.2.1 |
| F06 | Is the minimum duration of the emergency escape lighting at least 1 hour? |  | Yes No | BS EN 1038 4.2.5 |
| F07 | Is the ratio of illuminance (max to min) along the centre line of escape route(s) and open area lighting not greater than 40:1? |  | Yes No | BS EN 1038 4.2.2/4.3.2 |
| F08 | Does escape route lighting, open area lighting and safety signs achieve 50% of the required level within 5 secs and 100% within 60 secs? |  | Yes No | BS EN 1038 4.2.6/4.3.6/5.1 |
| F09 | For open area (anti-panic) lighting is the illuminance level at least 0.5 lx at floor level (excluding 0.5m around the perimeter of the area)? |  | N/A Yes No | BS EN 1038 4.3.1 |
| F10 | Is the minimum duration of the open area lighting at least 1 hour? |  | N/A Yes No | BS EN 1038 4.3.5 |
| F11 | In high risk areas, is the illuminance level at least 10% of the required level for that task, and, not less than 15 lx? |  | N/A Yes No | BS EN 1038 4.4.1 |
| F12 | Is the minimum duration of high risk lighting equal to at least the period for which the risk exists to people? |  | N/A Yes No | BS EN 1038 4.4.5 |
| F13 | Have high risk areas been provided with maintained luminaires or is the full required illuminance achieved within 0.5 secs? |  | N/A Yes No | BS EN 1038 4.4.6 |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| ILLUMINANCE OF SPECIFIC LOCATIONS |  |  |  |  |
| Is the minimum light level and duration achieved for the following specific locations: |  |  |  |  |
| G01 | KITCHENS 15 Lux for 30 Minutes |  | N/A Yes No | BS5266-1 Table E1 |
| G02 | FIRST AID ROOMS 15 Lux for 30 Minutes |  | N/A Yes No | BS5266-1 Table E1 |
| G03 | EXAMINATION & TREATMENT ROOMS 50 Lux for 30 Minutes |  | N/A Yes No | BS5266-1 Table E1 |
| G04 | REFUGE AREAS FOR PEOPLE WITH MOBILITY IMPAIRMENTS. 5 Lux for Full Rated Duration |  | N/A Yes No | BS5266-1 Table E1 |
| G05 | PLANT/SWITCH/WINDING ROOMS 15 Lux for Full Rated Duration |  | N/A Yes No | BS5266-1 Table E1 |
| G06 | FIRE ALARM CIE 15 Lux for Full Rated Duration |  | N/A Yes No | BS5266-1 Table E1 |
| G07 | RECEPTION AREAS 15 Lux for Full Rated Duration |  | N/A Yes No | BS5266-1 Table E1 |
| G08 | PANIC BARS/PADS/SECURITY DEVICES AT EXIT DOORS 5 Lux for Full Rated Duration |  | N/A Yes No | BS5266-1 Table E1 |
| G09 | SURROUNDS OF SWIMMING POOLS, SWIMMING AREAS, DIVING PLATFORMS & FLUMES 5 Lux for Full Rated Duration |  | N/A Yes No | BS 5266-1 Table E1 |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| REMEDIAL WORK |  |  |  |  |
| H01 | Do replacement luminaires meet the requirements of BS EN 60598-2-22? |  | N/A Yes No | BS 5266-1 Annex L3 |
| H02 | Have replacement batteries been checked for compatibility? |  | N/A Yes No | BS 5266-1 Annex L3 |
| H03 | Have replacement lamps been checked for compatibility? |  | N/A Yes No | BS 5266-1 Annex L3 |
| H04 | Where non-maintained luminaires have NOT been supplied from the local lighting circuit has the wiring been corrected or the fittings changed for maintained units? |  | N/A Yes No | BS 5266-1 Annex L3 |
| H05 | Where the wiring of central power supply systems does not offer adequate fire resistance, has additional fire protection been provided or the cable replaced? |  | N/A Yes No | BS 5266-1 Annex L3 |
| H06 | Have luminaires been cleaned where required and badly discoloured diffusers replaced? |  | N/A Yes No | BS 5266-1 Annex L3 |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| WORKMANSHIP |  |  |  |  |
| G01 | What is the standard of workmanship? |  | Good Satisfactory |  |
|  |  |  | Unsatisfactory Poor |  |
| Comments: |  |  |  |  |