# BS 5839-1:2017
Fire Detection & Fire Alarm Systems compliance checklist

Variations highlighted in bold type are considered to be potential system integrity or life threats and are not considered to be acceptable variations against the recommendations of BS 5839-1:2017.

If variations of this nature are identified during a site inspection, this could result in a major non-compliance being issued.

| Certificated / applicant company: |  |
| --- | --- |
| Company representatives: |  |
| Customer / user: |  |
| Location: |  |
| User representatives: |  |
| Restrictions made by user: (e.g. access and performance of tests) |  |
| Auditor: |  |
| Date of audit: |  |

| Applicable modules | System design |  |
| --- | --- | --- |
|  | Installation |  |
|  | Commissioning and handover (inc. verification) |  |

Note: This checklist does not cover maintenance

| Name of company undertaking system design: |  |  |  |
| --- | --- | --- | --- |
| A01 Module certificate issued: | Yes | No | N/A |
| Certificate number: |  |  |  |
| Date: |  |  |  |

| Name of company undertaking installation: |  |  |  |
| --- | --- | --- | --- |
| A01 Module certificate issued: | Yes | No | N/A |
| Certificate number: |  |  |  |
| Date: |  |  |  |

| Name of company undertaking commissioning & handover: |  |  |  |
| --- | --- | --- | --- |
| A01 Module certificate issued: | Yes | No | N/A |
| Certificate number: |  |  |  |
| Date: |  |  |  |

| A01 NSI Certificate of Select as appropriate issued: | Yes | No |
| --- | --- | --- |
| Certificate number: |  |  |
| Date: |  |  |

Record agreed variations below (or attach copy of certificate with list of variations):

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| DESIGN MODULE |  |  |  |  |
|  | Specified standards applied: |  |  |  |
| A01 | Has the correct NSI/BAFE certificate been issued within one month of completion of the system? |  | N/A Yes No | NSI Reg A5.1.4 |
| A02 | BS 5839 Category of system specified: |  |  | 5.2 8.2(a) |
| A03 | Additional standards specified (e.g. HTM05-03) |  |  | 5.2 8.2(a) |
|  | Specify whether system is Addressable (A) or Non-Addressable (N) |  | A N |  |
| A04 | Is the category of system appropriate and as specified in contract? |  | Yes No | 5 Annex A |
| A05 | Is the specified standby power supply period suitable for the category of system and the level of supervision? |  | Yes No | 25.4(e) |
| A06 | Does the system design proposal include all the required information? |  | Yes No | 8.2 |
| A07 | Has the system design taken into account any building regs (e.g. Part M) or Equality Act requirements? |  | N/A Yes No | 18 |
| A08 | Has an adequate O & M manual been provided detailing equipment, system configuration, cause/effect etc? |  | N/A Yes No | 40.2(b) |
| A09 | Are design battery capacity calculations available? |  | N/A Yes No | 25.4(e) Annex D |
| A10 | Have the correct quiescent and alarm currents been used? |  | N/A Yes No | 25.4(e) Annex D |
| Category M/L IQ at least 24 hours |  |  |  |  |
| IQ at least 6 hours if auto start generator |  |  |  |  |
| Category P IQ period of unoccupation + 24 hours up to 72 hours |  |  |  |  |
| IQ at least 24 hours if supervised (every six hours) or fault monitoring by ARC |  |  |  |  |
| A11 | Is the battery capacity, as designed, adequate? |  | N/A Yes No | 25.4(e) Annex D |
| A12 | Assumptions/variations drawn to customer's attention at design/quotation stage? |  | N/A Yes No | 7.2(a) |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| DOCUMENTATION |  |  |  |  |
| B01 | Are there satisfactory commissioning records? |  | N/A Yes No | 39.2(c) |
| B02 | Have BS 5839 certificates for design, installation, commissioning & acceptance been issued? (as applicable) |  | Yes No | 41.2(a)(b) |
| B03 | Is there a record of agreed variations? |  | N/A Yes No | 40.2(e) |
| B04 | Have suitable user instructions/manuals been provided to the customer? |  | N/A Yes No | 40.2(b) |
| B05 | Are there satisfactory 'as fitted' drawings? |  | N/A Yes No | 40.2(c) |
| B06 | Have 'as fitted' drawings been provided to the customer? |  | N/A Yes No | 40.2(c) |
| B07 | Has a logbook been provided to the customer? |  | N/A Yes No | 40.2(d) |
| B08 | Are insulation resistance test results available and satisfactory? (ELV wiring only) |  | N/A Yes No | 38.2(a) |
| B09 | Are test results for circuit parameters such as loop continuity available and satisfactory? |  | N/A Yes No | 38.2(d) |
| B10 | Have 230V supply test records been supplied by the electrical contractor/client? |  | N/A Yes No | 38.2(c) |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| INSTALLATION |  |  |  |  |
| C01 | Are cables of a suitable type? |  | N/A Yes No | 26.2(b)(d)(e) |
| C02 | Are cables with 'enhanced' fire resistance used where required? |  | N/A Yes No | 26.2(c) |
| C03 | Are cables adequately protected against mechanical damage? |  | N/A Yes No | 26.2(h)(k) |
| C04 | Are methods of cable support satisfactory? |  | N/A Yes No | 26.2(f) |
| C05 | Is there suitable segregation from other services and other fire alarm cables, where required? |  | N/A Yes No | 26.2 (l), (m),(n) |
| C06 | Are joints in cables terminated correctly? (applies only to joints external to FD&A system components) |  | N/A Yes No | 26.2(g) |
| C07 | Are all junction boxes suitably labelled? |  | N/A Yes No | 26.2(g) |
| C08 | Are fire alarm cables a single common colour? |  | N/A Yes No | 26.2(o) |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| MAINS POWER SUPPLIES |  |  |  |  |
| D01 | Has a suitable mains supply been provided? |  | N/A Yes No | 25.2 |
|  | Specifically: |  |  |  |
| D02 | Is the continuity of supply satisfactory? |  | Yes No | 25.2(a)(b)(h) |
| D03 | Is it a dedicated circuit? |  | Yes No | 25.2(b) |
| D04 | Has means of safe isolation been provided adjacent to all equipment requiring a mains supply? (see BS5839-1:2017, 29.2(e) Note 2) |  | N/A Yes No | 29.2(e) |
| D05 | Is labelling satisfactory? |  | Yes No | 25.2(f)(g) |
| D06 | Is the supply independent of any RCD protection? |  | Yes No | 25.2(i) |
| D07 | Is wiring of a suitable type and segregated? |  | Yes No | 26.2(b)(c) |
| D08 | Do mains supply cables enter the CIE separately? |  | N/A Yes No | 26.2(k) |
| D09 | Do separate mains supplies to other power supply units remote from the control and indicating equipment meet the above criteria? |  | N/A Yes No | 25.2(e) |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| CIRCUIT DESIGN |  |  |  |  |
| E01 | Does the area per loop satisfy the specified standards (addressable systems only)? |  | N/A Yes No | 12.2.2(c) |
| E02 | Is there adequate short circuit isolation (addressable systems only)? |  | N/A Yes No | 12.2.2(b) |
| E03 | Is there adequate tolerance to open circuit faults? |  | N/A Yes No | 12.2.2(b) |
| E04 | Are there at least two sounder circuits (or a suitable ring circuit with isolators)? |  | N/A Yes No | 12.2.2(j) 16.2.1(3i) |
| E05 | Are circuits monitored adequately? (e.g. are the correct indications given during fault conditions?) |  | Yes No | 12.2.1 |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| ZONING |  |  |  |  |
| F01 | Is the detection/alarm zoning adequate? |  | Yes No | 13/14 |
| F02 | Is a zone plan displayed? |  | N/A Yes No | 23.2.2(e) |
| F03 | Specifically, does the area per detection zone comply with specified standards? |  | Yes No | 13.2.3(a) |
| F04 | Does the search distance comply with specified standards? (60m maximum, but may not apply to addressable systems) |  | N/A Yes No | 13.2.3(b) 13.2.4(b) |
| F05 | Are MCPs assigned to the relevant accommodation zone? |  | N/A Yes No | 13.2.1(a) |
| F06 | Are staircases and other vertical shafts zoned separately? |  | N/A Yes No | 13.2.3(c) |
| F07 | Do the boundaries of alarm zones comprise fire-resisting construction (not external walls)? (phased evacuation only) |  | N/A Yes No | 14.2(a) |
| F08 | Do the boundaries of alarm zones coincide with the boundaries of detection zones? (phased evacuation only) |  | N/A Yes No | 14.2(d) |
| Comments: |  |  |  |  |

|  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- |
| MANUAL CALL POINTS |  |  |  |  |
| G01 | Are call points single action operation? |  | Yes No | 20.2(a) |
| G02 | Are call points fitted with protective covers? |  | Yes No | 20.2(b) |
| G03 | Is an “evacuate” signal sounded within 3 seconds of operation of any MCP? |  | Yes No | 20.2(c) |
| G04 | Is call point location and siting appropriate? |  | Yes No | 20.2(d) |
| G05 | Is there adequate provision of call points? |  | Yes No | 20.2 (e)(f)(g)(h) |
| G06 | Are call points mounted at the appropriate height? (1400mm above FFL ± 300mm)? |  | Yes No | 20.2(i) |
| G07 | Are call points sited to take into account the potential for accidental damage/operation and/or have they been fitted with suitable guards/covers where required? |  | N/A Yes No | 35.2.2(b) |
| G08 | Are suitable IP rated call points used in areas exposed to moisture? |  | N/A Yes No | 35.2.2(c) |
| G09 | Are call points sited to take into account the potential for malicious operation in shopping complexes, bars, etc? |  | N/A Yes No | 35.2.2(d) |
| G10 | Do call points remain operable when a detector is removed? |  | Yes No | 12.2.2(e1) |
| Comments: |  |  |  |  |

|  |  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- | --- |
| AUTOMATIC DETECTORS |  |  |  |  |  |
| H01 | Are the areas in which automatic fire detection is provided, sufficient for the category of system? |  |  | N/A Yes No | 8.2 |
| H02 | Are the types of detector used appropriate? |  |  | Yes No | 21.2 |
| H03 | Is detector spacing appropriate? |  |  | Yes No | 22.3 |
| H04 | Are ceiling heights within the limits for the detector type used? |  |  | Yes No | 22.9 |
|  | Is detector siting appropriate? |  |  | Yes No | 22.2 |
|  | Specifically, is siting/spacing satisfactory in relation to: |  |  |  |  |
| H05 | enclosed landings & stairways? |  |  | N/A Yes No | 22.2(b |
| H06 | shaft/riser openings into accommodation areas (except L4, L5 & P2)? |  |  | N/A Yes No | 22.2(c) |
| H07 | voids >800mm? |  |  | N/A Yes No | 22.2(d) 22.3(g) |
| H08 | lantern lights >800mm? |  |  | N/A Yes No | 22.2(e) |
| H09 | walls? |  |  | N/A Yes No | 22.3(g) |
| H10 | ceiling obstructions? |  |  | N/A Yes No | 22.3(i) |
| H11 | partitions & storage racks? |  |  | N/A Yes No | 22.3(j) |
| H12 | deep beams? |  |  | N/A Yes No | 22.3(k) |
| H13 | honeycomb ceiling? |  |  | N/A Yes No | 22.3(l) |
| H14 | perforated ceilings? |  |  | N/A Yes No | 22.3(m) |
| H15 | air conditioning/ventilation outlets? |  |  | N/A Yes No | 22.3(o) |
| H16 | clear space below detector (500mm)? |  |  | N/A Yes No | 22.3(p) |
| H17 | Have optical beam detectors been sited/installed to the recommendations of BS5839-1: 2017? |  |  | N/A Yes No | 22.5 |
| H18 | Are detectors sited at, or near, the apex of the roof? |  |  | N/A Yes No | 22.3(d) |
| H19 | Are the detectors mounted within the appropriate limits below the ceiling? |  |  | Yes No | 22.3(e) |
| H20 | Are remote indicator lamps provided where required? |  |  | N/A Yes No | 13.2.5 |
| H21 | If BS 6266 is specified, are the specific recommendations for detector type, spacing and siting satisfied? |  |  | N/A Yes No | BS 6266 |
| H22 | If BS 7273-1 is specified, are the specific recommendations for detector type, spacing and siting satisfied? (Interfaces for suppression systems) |  |  | N/A Yes No | BS 7273-1 |
| H23 | If BS 7273-4 is specified are the recommendations satisfied? |  |  | N/A Yes No | BS 7273-4 |
| H24 | If BS 7273-6 is specified are the recommendations satisfied? |  |  | N/A Yes No | BS 7273-6 |
| Comments: |  |  |  |  |  |

|  |  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- | --- |
| AUDIBLE AND VISUAL ALARMS |  |  |  |  |  |
| J01 | Does the sounder layout appear suitable for the sound levels required? |  |  | N/A Yes No | 16.2.1 |
| J02 | Have sound levels been measured and any shortfalls identified? |  |  | N/A Yes No | 39.2(c5) |
| J03 | Are the sounders of an appropriate type (e.g. in relation to frequency)? |  |  | Yes No | 16.2.1(b)(c) |
| J04 | Where music levels >80dB(A), is the music muted when the alarm sounds? |  |  | N/A Yes No | 16.2.1(d) |
| J05 | Can the fire service be summoned without interference from the fire alarm system? |  |  | N/A Yes No | 15.2(c) |
| J06 | Do sound levels in hospitals comply with HTM 05-03 (Part B) or SHTM 82? |  |  | N/A Yes No | 16.2.3(a) |
| J07 | Have visual alarms been provided where required? |  |  | N/A Yes No | 17.2(a |
| J08 | Does the provision of fire alarm warnings for people with impaired hearing meet the recommendations of clause 18.2? |  |  | N/A Yes No | 18.2 |
| J09 | Are visual alarm devices compliant with BS EN54-23 and sited accordingly? |  |  | N/A Yes No | 11.2(o) 17.2(e)(f) |
| J10 | Are the visual alarms adequate in terms of colour and siting? |  |  | N/A Yes No | 17(b-f) |
| J11 | Is an external sounder/visual alarm provided if required? |  |  | N/A Yes No | 16.2.1(f) |
| Comments: |  |  |  |  |  |

|  |  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- | --- |
| CONTROL AND INDICATING EQUIPMENT |  |  |  |  |  |
| K01 | Is compliance with EN54-2 and EN54-4 claimed? (or equivalent part to BS 5839) |  |  | Yes No | 11.2(m)(p) |
| K02 | Are functional requirements of EN54 satisfied? (or equivalent part to BS 5839) |  |  | Yes No | 39.2(c8) |
| K03 | Is the siting appropriate? |  |  | Yes No | 23.2.1 (a)(b)(g) |
| K04 | Is the area in which equipment sited protected by automatic detection (if required)? |  |  | N/A Yes No | 23.2.1(f) |
| K05 | Is internal workmanship satisfactory? |  |  | Yes No |  |
| K06 | Are batteries for standby power supplies of a suitable type? |  |  | Yes No | 25.4(b) |
| K07 | Are batteries marked with date of installation and can dates be read without disturbing the batteries? |  |  | Yes No | 25.4(c) |
| K08 | Have the quiescent & alarm currents been verified at commissioning? |  |  | Yes No | 39.2(c21) |
| K09 | Have the quiescent & alarm currents been verified for additional PSUs? |  |  | N/A Yes No | 39.2(c21) |
| K10 | Is the battery capacity, as installed, adequate? |  |  | N/A Yes No | 25.4(e) |
| K11 | Is the wiring to any separate power supply equipment/battery enclosures of a suitable type? |  |  | N/A Yes No | 26.2(b) |
| K12 | Are the connections to power supply equipment in separate housings duplicated? |  |  | N/A Yes No | 12.2.2(l) |
| K13 | Are PSU/batteries in separate enclosures from the CIE fused at the remote end? |  |  | N/A Yes No | 12.2.2(l) |
| K14 | Do batteries connected in parallel give the correct fault indications? |  |  | N/A Yes No | 12.2.1(d) |
| K15 | Is the rating of the charger sufficient to recharge the batteries within 24 hours? |  |  | N/A Yes No | 25.4(d) |
| Comments: |  |  |  |  |  |

|  |  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- | --- |
| REMOTE TRANSMISSION OF ALARMS |  |  |  |  |  |
| L01 | Is the FD&A system provided with an ATS? |  |  | N/A Yes No | 15.2 (e)(f)(g)(h) |
| L02 | Is the telephone switch room or frame room protected by AFD? |  |  | N/A Yes No | 15.2(j) |
| L03 | If “Cat P” is a fault signal transmitted in addition to fire signals, where required? |  |  | N/A Yes No | 25.4(e3) |
| L04 | For Cat P systems, if no fault signal is transmitted, is the battery standby capacity sufficient to maintain the system for at least 24 hours longer that the unoccupied area (max 72 hours)? |  |  | N/A Yes No | 25.4(e4) |
| L05 | Is the wiring to/from the transmitter of a satisfactory type and monitored? |  |  | N/A Yes No | 15.2(l) |
| L06 | If a dedicated fire ATS is provided, does the 230Vac supply and the standby supply to the ATS meet the requirements of clause 25? |  |  | N/A Yes No | 15.2(m) |
| L07 | Is the ATS PSU monitored for the required fault conditions by the CIE? |  |  | N/A Yes No | 12.2.1 |
| L08 | If fire alarm signals are transmitted via the intruder ATS, is the standby battery capacity of the intruder ATS sufficient for the category of system? |  |  | N/A Yes No | 15.2(n) |
| L09 | Is the ARC used to monitor fire signals certificated to BS 5979 / BS EN 50518 / BS 8591/BS 9518 and does it have monitoring of fire signals within its scope? |  |  | N/A Yes No | 15.2(i) |
| Comments: |  |  |  |  |  |

|  |  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- | --- |
| ANCILLARY SERVICES |  |  |  |  |  |
| M01 | Confirm that power is not supplied from the fire alarm system in the quiescent state? |  | N/A Yes No |  | 9.2(d) |
| Comments: |  |  |  |  |  |

| LIMITATION OF FALSE ALARMS |  |  |  |
| --- | --- | --- | --- |
| N01 | Has the correct type of detector been specified in each location to minimise the potential for false activations? | Yes No | 35.2.3(a)(b)(c)(d)(e) |
| N02 | Have optical beams detectors been installed and sited correctly to minimise the potential for false activations? | N/A Yes No | 35.2.3(g)(h) |
| N03 | Are ASD systems configured for the correct level of sensitivity? | N/A Yes No | 35.2.3(j) |
| N04 | Are carbon monoxide detectors sited to minimise the potential for false activations? | N/A Yes No | 35.2.3(k)(l) |
| N05 | Are flame detectors sited to minimise the potential for false activations? | N/A Yes No | 35.2.3(m) |
| N06 | Is system type appropriate to limit false alarms? | N/A Yes No | 35.2.4 |
| N07 | Are suitable filtering measures applied? | N/A Yes No | 35.2.7.2 |
| N08 | Filtering has not been applied to call points, heat detectors or sprinkler systems. | N/A Yes No | 35.2.7.2(b) |
| N09 | Is the change of state in time related systems an automatic function? | N/A Yes No | 35.2.7.2(c) |
| N10 | Have measures been taken to prevent false activations being initiated by automatic sprinkler systems? | N/A Yes No | 35.2.7.2(g) |
| Comments: |  |  |  |

|  |  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- | --- |
| RADIO LINKED FIRE DETECTION SYSTEMS |  |  |  |  |  |
| P01 | Has a comprehensive radio survey taken place PRIOR to the installation commencing? |  | Yes No |  | 27.2(g) |
| P02 | Have records of signal strength readings and background noise levels taken at time of survey been retained for future reference? |  | Yes No |  | 27.2(g4) |
| P03 | Do components comply with BS EN 54-25? |  | Yes No |  | 27.2(a) |
| P04 | Are all radio linked components supplied from at least two independent power supplies? |  | Yes No |  | 27.2(b) |
| P05 | Do power supplies for radio CIE meet the recommendations of clause 25? |  | Yes No |  | 25.2 |
| P06 | Are antennae cables monitored for open and short circuit conditions? |  | Yes No |  | 27.2(c) |
| P07 | Do antennae cables external to components meet the recommendations of clause 26.2? |  | N/A Yes No |  | 27.2(d) |
| P08 | Does the activated detector continue to give a visual indication for at least 20 minutes after the activation (unless the CIE has been reset)? |  | Yes No |  | 27.2(f) |
| P09 | Do commissioning records include information relating to the system coding and details of the received signal levels for ALL radio devices and the background noise level? |  | N/A Yes No |  | 27.2(i) |
| P10 | Are records of signal levels kept on site with the system log book? |  | Yes No |  | 27.2(k) |
| Comments: |  |  |  |  |  |

|  |  |  |  |  | Relevant standard & clause (where applicable) |
| --- | --- | --- | --- | --- | --- |
| WORKMANSHIP |  |  |  |  |  |
| Q01 | What is the standard of workmanship? |  | Good Satisfactory |  |  |
|  |  |  | Unsatisfactory Poor |  |  |
| Q02 | Does the system conform to BS 7671 (as far as can be ascertained)? |  | Yes No |  | 37.2(a) |
| Q03 | Are cables securely fixed at the correct intervals with fire resistant fixings and are they supported above suspended ceilings? |  | Yes No |  | 37.2(B) |
| Q04 | Are cable holes fire stopped? |  | N/A Yes No |  | 37.2(l)(m) |
| Comments: |  |  |  |  |  |