TYPICAL INSTALLATIONS LIMITED

(Typical installations normal letterhead)

System Design Proposal

| Client Address | Site Address |
| --- | --- |
| Proposed Specification No:- |  |
| Issue Number |  |
| Site Survey/Risk Assessment No:- |  |
| Dated:- |  |

This intruder alarm system is to be installed to conform to PD 6662:2017 (which is the UK Scheme for the application of the European Standard EN 50131), BS 8243, and NSI Codes of Practice. The system is capable of generating Sequentially Confirmed Alarms, for the purposes of obtaining Police response. Please read the section on Confirmation technology attached to this proposal.

Grading of Intruder and Hold up Alarm Systems

In accordance with the European Standard Technical Specification DD CLC/TS 50131-7:2010, a site survey and risk assessment of your property has been carried out. The risk assessment relates solely to the grading and design of the proposed intruder alarm and is based upon information available at the time of survey. Therefore, the grade for this installation has been specified as – Grade 2, with notification option F. All equipment fitted will conform to EN 50131 - Grade 2 or higher

(Please ensure that this is acceptable to your building and contents insurer)

Upon completion of the installation a National Security Inspectorate (NSI) “Certificate of Compliance” will be issued.

Premises

The premises of XXXXXX consists of a large (100 m x 25 m) single story commercial workshop of concrete block construction up to 2 m high with steel frame and double skinned metal cladding above, with single storey brick built offices and amenities attached.

Detection areas and devices

For the purposes of this proposal and specification, the sighting of all equipment is as seen from outside the final exit door facing the building.

NOTE – because it is not possible to determine at the time of the site survey the nature and structure of the building, the hidden pipe work and cabling, the exact final location of equipment and the allotment of zones may be amended by the installing engineer in agreement with the customer at the time of install.

All equipment will meet environmental class II unless otherwise stated in this specification.

Item 1	Front door

Device	Magnetic door contact

Location	Fitted to leading edge of front door near the top

Detection	To detect the door opening more than 100 mm

Programmed as	Final exit door – (this will act as the final setting point of the system and will also initiate the 20 second entry timer)

Inhibit	The user is not able to inhibit this circuit.

Confirmation	NOTE – the opening of this door will inhibit confirmation during the entry time.

Item 2	Reception area

Device	Passive infrared detector

Location	Far right hand corner at ceiling height

Detection	12 m by 90 degrees to detect movement in the general area

Programmed as	Walk through area

Inhibit	The user is able to inhibit this circuit

Confirmation	NOTE - This detector will not contribute to a confirmed alarm if the entry door has been opened and the entry timer has started

Item 3	Accounts office

Device	Dual technology detector

Location	Far right hand corner at ceiling height

Detection	12 m by 90 degrees to detect movement in the general area

Programmed as	Instant alarm area

Inhibit	The user is not able to inhibit this circuit.

Confirmation	This detector is capable of contributing to a confirmed alarm

Item 4	Accounts office

Device	Dual technology detector

Location	Far left hand corner at ceiling height

Detection	12 m by 90 degrees to detect movement in the general area

Programmed as	Instant alarm area

Inhibit	The user is not able to inhibit this circuit.

Confirmation	This detector is capable of contributing to a confirmed alarm

Item 5	General office

Device	Passive infrared detector

Location	Near left hand corner at ceiling height

Detection	12 m by 90 degrees to detect movement in the general area

Programmed as	Instant alarm area

Inhibit	The user is able to inhibit this circuit

Confirmation	This detector is capable of contributing to a confirmed alarm

Item 6	Main workshop - eastern end

Device	Dual technology detector

Location	Front left hand corner at manufacturer’s recommended height

Detection	Range = 15 m x 110 degrees. Please note this detector is designed to detect movement around the fire exit and roller shutter door. It will NOT detect movement over the full works area.

Programmed as	Instant alarm area

Inhibit	The user is able to inhibit this circuit

Confirmation	This detector is capable of contributing to a confirmed alarm

Item 7	Main workshop - western end

Device	Dual technology detector

Location	Front right hand corner at manufacturer’s recommended height

Detection	Range = 15 m x 110 degrees. Please note this detector is designed to detect movement around the staff entrance and loading bay. It will NOT detect movement over the full works area.

Programmed as	Instant alarm area

Inhibit	The user is able to inhibit this circuit

Confirmation	This detector is capable of contributing to a confirmed alarm

Item 8	Main workshop – Roller shutter door

Device	2 off Magnetic door contacts

Location	Fitted to the lower edge of the door one mounted near the left hand corner and the other mounted near the right hand corner

Detection	To detect the door opening more than 100 mm

Programmed as	Instant alarm area

Inhibit	The user is able to inhibit this circuit.

Confirmation	This pair of detectors are capable of contributing to a confirmed alarm

Item 9	Main workshop – staff entrance door

Device	Magnetic door contact

Location	Fitted to leading edge of front door near the top

Detection	To detect the door opening more than 100 mm

Programmed as	Final exit door – (this will act as the final setting point of the system and will also initiate the 20 second entry timer)

Inhibit	The user is not able to inhibit this circuit.

Confirmation	NOTE – the opening of this door will inhibit confirmation during the entry time.

Control equipment

The system will be controlled by a 16-zone Control panel located within the stationery cupboard behind the reception desk, conforming to current Grade 2 security requirements, and will be operated by 2 remote keypads.

The System will have a standby battery mounted within the main control panel and provide 12 hours of operation in case of a mains failure.

Mains power supply (Customer responsibility)

A suitably rated (3 amp) un-switched fused spur should be provided within the stationery cupboard to provide mains power for the system. As agreed this should be provided by the works electrician prior to the commencement of the installation and should be sited to allow the installing engineer room to position the control unit.

Remote keypads (RKPs)

RKP 1

Location	Sited at a convenient height in the reception area at a location that will avoid viewing from the exterior of the premises.

Display screen	LCD (Liquid Crystal Display)

Digital Key Reader	Yes (see notes on setting and un-setting)

Facilities	Manager and user

RKP 2

Location	Sited just inside the rear main works staff entrance in a position to enable ease of use and to be free from accidental damage caused by stock, stores, forklift trucks etc.

Display screen	LED display, giving limited information.

Digital Key Reader	Yes (see notes on setting and un-setting)

Facilities	User only

Notification and Warning Devices

Primary notification will be by XXXXXXXX, located inside the main control panel fitted in the stationery cupboard. This offers a “dual path” communication (one Alarm Transmission System (ATS) with two transmission paths) with each path being monitored for fault conditions.

The device will pass all relevant signals to XXXXXXXX, an NSI approved Alarm Receiving Centre.

By default the user setting the system will not be notified if a single path failure exists on the ATS. The system can be configured to notify the user setting the system of the existence of a single path failure if this is required. Failure of both alarm transmission paths will always be notified to the user setting the system.

Secondary notification (audible warning devices)

AWD 1

Device	A self-actuating sounder in a polycarbonate housing with the
alarm company logo.

Location	High up at the front of the building above the main entrance.

Audible alarm warning	82 decibel sounder.

Visual alarm warning	Blue flashing strobe which will continue to flash after the

sounder cuts out.

Tamper	24 hr active tamper switch to detect the removal of the box lid
and removal of box from wall.

Environmental	Class IV

AWD 2

Device	A self-actuating sounder in a polycarbonate housing with the
alarm company logo.

Location	High up at the rear of the building above the main roller shutter
works door.

Audible alarm warning	82 decibel sounder.

Visual alarm warning	Blue flashing strobe which will continue to flash after the

sounder cuts out.

Tamper	24 hr active tamper switch to detect the removal of the box lid
and removal of box from wall.

Environmental	Class IV

Additional audible indications

Device 1	12 volt loudspeaker.

Location	In the reception area at ceiling height above the RKP.

NOTE	This device also acts as an audible indication for setting,

unsetting and alert indications

Device 2	12 volt loudspeaker

Location	At ceiling height above the RKP near the staff entrance.

NOTE	This device also acts as an audible warning for setting,

unsetting and alert indications.

Extras

There will also be two “dummy” or “decoy” Bell Boxes, these will be fitted high up (out of reach) at each end of the building.

Note: - To conform to the requirements of EN 50131-1 audible warning devices are time limited to a maximum of 15 minutes. The sounders will become active again following the reinstatement of the system.

Parameters and Operation

Planned Responses and Interventions

The table below details the planned responses to the alarm activations and other possible notifications by the Alarm Receiving Centre.  These have been proposed for your intruder alarm system. The table prescribes what the response will occur for each activation in both the unset condition and the set condition.

| Activation | Unset | Set |
| --- | --- | --- |
| Fire | The Fire and rescue service will be contacted. Their response is dependent upon the Alarm Receiving Centre filtering procedure and the local fire service attendance policy for your type of building/use and its previous alarm history. | The Fire and rescue service will be contacted. Their response is dependent upon the Alarm Receiving Centre filtering procedure and the local fire service attendance policy for your type of building/use and its previous alarm history. |
| Activation | Unset | Set |
| Personal Attack (Hold up) | The Police will be contacted | The police will be contacted |
| Intruder | Not permitted | The nominated key holder(s) will be contacted. |
| Open and close or miss-operation | When you unset the system a signal will be sent and logged at the alarm receiving centre. | When you set the system a signal will be sent and logged at the alarm receiving centre. |
| Circuit Inhibit/Reinstatement | Not permitted | If a detector has been activated and another detector has not activated within the confirmation time then the system will be re-instated but the detector will be inhibited. The Key holder will be contacted to be informed of this condition. |
| General Fault | If the alarm system has a fault then the ARC will contact the key holder dependent upon client request | If the alarm system has a fault then the ARC will contact the key holder |
| Confirmed alarm | Not permitted | The alarm receiving centre will following a filtering delay of up to 120 seconds contact the police. |
| Tamper | The alarm receiving centre will contact the key holder | The alarm receiving centre will contact the key holder. If this follows an intruder signal or precedes an intruder signal then it will contribute to a confirmed alarm. |
| Transmission Line Fault | The alarm receiving centre will contact the key holder | The alarm receiving centre will contact the key holder. If this follows an intruder signal or precedes an intruder signal then it will contribute to a confirmed alarm. |
| Mains Fail | The alarm receiving centre may contact the key holder dependent upon request of the client | The alarm receiving centre will contact the key holder immediately or following a defined delay dependent upon client request |

Setting, part setting, unsetting and re-setting after alarm.

Note - Digital Key - These are electronic key fob devices that replace the need for codes so that the alarm setting / unsetting process can be managed by means of a single action.

Completion of Setting	BS 8243, option 6.3.c (Door Contact on Final Exit Door)

The setting sequence is started by presenting a Digital Key to the Remote Keypad, and completed by the closing of the final exit door. There is no specified exit time.

Part setting

The system has the facility for the office staff to set / unset their own part of the system and the works staff to set / unset the works part of the system independently of each other.

Please note – the system is not fully set until all parts of the system have been set. There will be no confirmation system and no police response until the system is fully set.

Unsetting - Entry time = 10 seconds – BS 8243, option 6.4.5 (Digital Key)

The unsetting sequence is started when an initial entry door is opened and the sequence is completed by presenting the Digital Key to the Remote Keypad within the entry time limit.

Opening the entry door starts the entry timer and confirmed alarms will not be possible during the entry time.  The system is then unset by means of the digital key.  However, confirmed alarms are possible if the system is not unset and the entry timer expires.

If an alarm condition occurs off the entry route during the entry time then the alarm is indicated and a 30 second timer starts.  If the system is not unset, a confirmed alarm will occur when both the entry time and the 30 second timer expire.

If an alarm condition occurs before the entry time is started then this will start the confirmation timer, and if the entry time expires before the alarm system is unset a confirmed alarm will occur provided this is within the confirmation time of 30 minutes.

Note: If the digital key fails to unset the system, it will be possible to complete the unsetting by means of a user code, but only after the entry time has expired. This action should only be used as an exception and evidence of repeated use of the code to unset may affect both police response and your insurance.

Users should exercise care when using the method of unsetting described in BS 8243 6.4.5 as it is possible to generate false confirmed intruder alarms if a detector not on the entry route is activated during or after the entry timer expires, which will in turn lead to a waste of police time and possible loss of police response.

System users

The system offers up to 100 different users on different levels of access, these are -

Staff codes (Digital Key) – (equal to EN 50131-1 user access level 2)

Each Digital Key is programmed to allow the staff to set, unset, part set and reset after non-policed activations.

Manager codes (Digital Key) – (equal to EN 50131-1 user access level 2)

Each Digital Key is programmed to allow the alarm manager to set, unset and reset same as the staff, but will also allow various other limited programming functions.

Engineer codes – (equal to EN 50131-1 user access level 3)

These codes allow the alarm servicing company to set the system parameters and functions and to carry out servicing and engineering work without creating an alarm.

Please note – the level 3 engineer access codes cannot be used without prior authorisation by a user or manager Digital Key or, level 3 access codes may be used without prior authorisation if the I&HAS is unset and the user to be given access at level 3 is at the supervised premises and accesses the CIE locally. When this option is used notification will be given by a warning device and remotely, i.e. by the ATS, when access is granted.

Inhibiting/isolating detectors

The control panel has the facility to allow selected users to inhibit/isolate individual detectors or zones to allow for temporary work to be carried out or following accidental or storm damage to the building or any other suitable reasons. The benefit is that the rest of the system can still be used even if one or more detection device is out of action.

Note – It must be remembered that there will be no active alarm and no police response in areas where a detector has been omitted. Therefore there may not be any insurance cover on that area. Please check that this is acceptable to your insurer.

The ability to enable detectors or zones to be inhibited lies with the alarm company and is decided by agreement between the alarm company and the customer.

Information on Confirmation as required by BS 8243

In order to reduce false alarms and to ensure there is a high probability of a genuine activation, under the current police (NPCC) policy, the police will only respond to confirmed alarms.

Sequential confirmation, as specified by Typical Installations, requires that two separate detectors on independent circuits activate, within a pre-defined time window, before a confirmed alarm condition can be notified. Therefore the system has been designed with the intention that an intruder will probably activate at least two detectors before reaching any desirable stock or valuables.

If a single detector activates the alarm, this will be transmitted to an Alarm Receiving Centre

(ARC) who will inform the keyholders, but it will not pass the alarm to the police.

If a second activation occurs on a different detector within the confirmation time of 30 minutes, the system will send a confirmed alarm signal to the ARC, who will then contact the police.

At the end of the confirmation time, if a second activation has not occurred, the system will reinstate and the 30 minute confirmation time window will start again. At the time of reinstatement if a detector is still active, the system will inhibit that detector and a signal will be passed to the ARC who will inform the keyholders.

Note: - Once a confirmed alarm has been passed to the ARC the system must be restored by the alarm company operative and not by the keyholder.

Important! A requirement of BS 8243

Due to the previous high incidence of customer error and accidental activation upon entry, your attention is drawn to the fact that if an intruder succeeds in forcing open the initial entry door, a confirmed alarm cannot be generated until the entry time has expired.

Pricing structure

All parts are covered by manufacturer’s warranties, and labour along with monitoring costs for the first year are included in the installation price, apart from the exceptions shown in our terms and conditions.

Installation Price = £	(plus VAT)

Service and / or Maintenance

Preventative maintenance and corrective maintenance will be provided in accordance with the requirements of BS 9263:2016, DD CLC/TS 50131-7:2010 and the terms and conditions of our maintenance contract. Preventative maintenance will consist of 2 site visits per annum to be carried out on a 6 monthly basis.

Should you require any help or assistance during normal office hours, please contact us on 010XX 100100. For emergency repairs out of hours please call 070XX 700700.

Service and Maintenance Options

Both service and maintenance options are payable after the first 12 months and are payment in advance for the next 12 months, the payment is then due every year on the anniversary of installation.

Please choose an option

Option A

Option A includes the annual monitoring charge to the Alarm Receiving Centre, all parts and labour costs for that year that occur through fair wear and tear and the costs of 2 service or maintenance visits per year by the alarm engineer.

Price for option A = £

Option B

Option B includes the annual monitoring charge to the Alarm Receiving Centre, and the costs of 2 service or maintenance visits per year by the alarm engineer.

NOTE – Under option B (after the first 12 months) all other parts and labour charges will be made at the company’s current charge rates.

Price for option B = £