TYPICAL INSTALLATIONS LIMITED

(Typical installations normal letterhead)

System Design Proposal

| Site address |  |
| --- | --- |
| Quote reference |  |
| Issue number | 1 |
| Date (dd/mmm/yyyy) |  |

This intruder alarm system is to be installed to conform to PD 6662:2017 (which is the UK Scheme for the application of the European Standard EN 50131), BS 8243, and NSI Codes of Practice. The system is capable of generating Sequentially Confirmed Alarms for the purposes of obtaining Police response.

Security Grading of Intruder and Hold-up Alarm Systems

In accordance with the European Standard Technical Specification DD CLC/TS 50131-7:2010, a site survey and risk assessment of your property has been carried out, (reference nnnnnnn). The risk assessment relates solely to the security grading and design of the proposed intruder alarm and is based upon information available at the time of survey. Therefore, the security grade for this installation has been specified as – Grade 2, with notification option F. All equipment fitted will conform to EN 50131 – security Grade 2 or higher

All equipment will meet environmental class II unless otherwise stated in this system design proposal.

(Please ensure that this is acceptable to your building and contents insurer)

Upon completion of the installation, a National Security Inspectorate (NSI) “Certificate of Compliance” will be issued.

Premises

The premises of XXXXXX consists of a single story commercial workshop and office of concrete block construction up to 2 m, with steel frame and double skinned metal cladding above.

Unsetting method

The intruder alarm system will use BS 8243, unsetting option 6.4.5 (Digital Key).

The unsetting sequence is started when an initial entry door is opened and the sequence is completed by presenting the Digital Key to the Remote Keypad within the entry time limit.

Opening the entry door starts the entry timer and confirmed alarms will not be possible during the entry time. The system is then unset by means of the digital key. However, confirmed alarms are possible if the system is not unset and the entry timer expires.

If an alarm condition occurs off the entry route during the entry time then the alarm is indicated and a 30 second timer starts. If the system is not unset, a confirmed alarm will occur when both the entry time and the 30 second timer expire.

If an alarm condition occurs before the entry time is started then this will start the confirmation timer and, if the entry time expires before the alarm system is unset, a confirmed alarm will occur provided this is within the confirmation time of 30 minutes.

Note: If the digital key fails to unset the system, it will be possible to complete the unsetting by means of a user code but only after the entry time has expired. This action should only be used as an exception and evidence of repeated use of the code to unset may affect both police response and your insurance.

Equipment and location

For the purposes of this proposal, the sighting of all equipment is as seen from outside the final exit door facing the front of the building.

All intruder detection devices contribute to confirmation unless otherwise stated in this proposal.

All intruder devices can be inhibited by a user unless otherwise stated in this proposal.

Note: It must be remembered that there will be no active alarm and no police response in areas where a detector has been omitted. Therefore there may not be any insurance cover on that area. Please check that this is acceptable to your insurer.

Entry route detection

Setting will be completed by the closure of the final entry detector. Once the intruder system is set, opening the initial entry detector will commence the entry process having an entry time of 20 seconds.

Front office door

Final exit and initial entry detector

Item 1

A magnetic door contact will be fitted to the leading edge near the top of the door to detect the opening of the door.

This detector cannot be inhibited by a user.

Reception lobby

Item 2

A passive infrared detector with a detection area of 12 metres by 89° angle from the detector will be fitted in the near right hand corner mounted at a height of 1.8 metres to detect movement in the general area.

Detection off the entry route

Accounts office

Item 3

A passive infrared detector with a detection area of 16 metres by 89° angle from the detector will be fitted in the near right hand corner mounted at a height of 1.8 metres to detect movement in the general area.

Item 4

A dual technology detector with a detection area of 16 metres by 86° angle from the detector will be fitted in the near left hand corner mounted at a height of 1.8 metres to detect movement in the general area.

General office

Item 5

A passive infrared detector with a detection area of 16 metres by 89° angle from the detector will be fitted in the near right hand corner mounted at a height of 1.8 metres to detect movement in the general area.

Forman’s office

Item 6

A dual technology detector with a detection area of 12 metres by 86° angle from the detector will be fitted in the near left hand corner mounted at a height of 1.8 metres to detect movement in the general area.

Workshop

Item 7

A dual technology detector with a detection area of 24 metres by 86° angle from the detector will be fitted in the near left hand corner mounted at a height of 2.1 metres to detect movement in the area of the milling machines.

Item 8

A dual technology detector with a detection area of 24 metres by 86° angle from the detector will be fitted in the far right hand corner mounted at a height of 2.1 metres to detect movement in the area fitting work benches.

Item 9

A dual technology detector with a detection area of 24 metres by 86° angle from the detector will be fitted in the Centre of the far wall mounted at a height of 2.1 metres to detect movement in the area of the central passage.

Item 10

2 off magnetic door contacts to be fitted to the lower edge of the near roller door 100mm in from each corner to detect opening of the door.

Note: This pair of detectors will contribute to confirmation as a single detection circuit.

Item 11

2 off magnetic door contacts to be fitted to the lower edge of the far roller door 100mm in from each corner to detect opening of the door.

Note: This pair of detectors will contribute to confirmation as a single detection circuit.

Control and Indicating equipment

Control panel

The intruder and hold-up alarm system will be controlled by a 16-zone control panel located within the stationery cupboard adjacent to the workshop door in the general office. This control panel will be configured to comply with security BS EN 50131-1 Grade 2

The system will have a standby battery mounted within the main control panel to provide a minimum of 12 hours operation in a case of a mains failure.

A cloud service will be configured to allow the unsetting and setting of the intruder system via a smart phone (remote device).

IMPORTANT

If using a remote device to remotely set/unset your intruder alarm system, your attention is drawn to the fact that, whenever a premises is unattended but its intruder alarm system(s) is (are) not fully set, any related insurance cover might be inoperative. For advice on this matter, it is recommended that you consult your insurer(s).

Remote keypad

A remote keypad will be mounted in the reception lobby adjacent to the entry door, providing user with control of the intruder and hold-up alarm system. This keypad includes a digital key reader for the purpose of setting and unsetting the intruder alarm system.

4 proximity fobs compatible with the digital key reader will be provided to be used to set and unset the intruder alarm system.

Notification equipment

A dual path supervised premises transceiver, meeting the BS EN 50136-1 alarm transmission system performance category of DP2, will be fitted with in the control panel and will be monitored by xxxxxxxx, an NSI approved Alarm Receiving Centre.

A self-actuating sounder incorporating a flashing strobe light will be fitted externally to the front elevation of the premises at a level out of reach to avoid sabotage or vandalism. The sounder will sound for 15 minutes after an alarm activation. The strobe light will continue to flash until the system is reset or the confirmation timer is reinstated. The sounder cut-off timer will reset when the confirmation timer is reinstated or the system is reset.

Planned responses and interventions

The table below details the planned responses to the alarm activations and other possible notifications by the Alarm Receiving Centre. These have been proposed for your intruder alarm system. The table prescribes what the response will be for each activation in both the unset condition and the set condition.

| Activation | Unset | Set |
| --- | --- | --- |
| Unconfirmed alarm | Not permitted | The nominated key holder(s) will be contacted. |
| Open and close or miss-operation | When you unset the system, a signal will be sent and logged at the Alarm Receiving Centre. | When you set the system, a signal will be sent and logged at the Alarm Receiving Centre. |
| Circuit inhibit/reinstatement | Not permitted | If a detector has been activated and another detector has not activated within the confirmation time, then the system will be reinstated but the detector will be inhibited. The key holder will be contacted to be informed of this condition. |
| General fault | If the alarm system has a fault, then the ARC will contact the key holder dependent upon client request. | If the alarm system has a fault, then the ARC will contact the key holder. |
| Confirmed alarm | Not permitted | The Alarm Receiving Centre will, following a filtering delay of up to 120 seconds, contact the police. |
| Tamper | The Alarm Receiving Centre will contact the key holder. | The Alarm Receiving Centre will contact the key holder. If this follows an intruder signal or precedes an intruder signal, then it will contribute to a confirmed alarm. |
| Transmission line fault | The Alarm Receiving Centre will contact the key holder. | The Alarm Receiving Centre will contact the key holder. If this follows an intruder signal or precedes an intruder signal, then it will contribute to a confirmed alarm. |
| Mains fail | The Alarm Receiving Centre may contact the key holder dependent upon request of the client. | The Alarm Receiving Centre will contact the key holder immediately or following a defined delay dependent upon client request. |

Customer responsibilities

A 3 amp un-switched fused electrical spur located in the stationary cupboard to provide mains power for the alarm system control panel

Note: Because it is not possible to determine at the time of the site survey the nature and structure of the building, the hidden pipe work and cabling, the exact final location of equipment and the allotment of zones may be amended by the installing engineer in agreement with the customer at the time of install.

Pricing structure

All parts are covered by manufacturer’s warranties and labour along with monitoring costs for the first year are included in the installation price apart from the exceptions shown in our terms and conditions.

Installation Price = £	(plus VAT)

Service and/or maintenance

Preventative maintenance and corrective maintenance will be provided in accordance with the requirements of BS 9263:2016, DD CLC/TS 50131-7:2010 and the terms and conditions of our maintenance contract. Preventative maintenance will consist of 2 site visits per annum to be carried out on a 6-monthly basis.

Should you require any help or assistance during normal office hours, please contact us on 010XX 100100. For emergency repairs out of hours, please call 070XX 700700.

Service and maintenance options

Both service and maintenance options are payable after the first 12 months and are payment in advance for the next 12 months. The payment is then due every year on the anniversary of installation.

Please choose an option

Option A

Option A includes the annual monitoring charge to the Alarm Receiving Centre, all parts and labour costs for that year that occur through fair wear and tear and the costs of 2 service or maintenance visits per year by the alarm engineer.

Price for Option A = £

Option B

Option B includes the annual monitoring charge to the Alarm Receiving Centre and the costs of 2 service or maintenance visits per year by the alarm engineer.

Note: Under Option B (after the first 12 months) all other parts and labour charges will be made at the company’s current charge rates.

Price for Option B = £